## Buyer Info
Appendix 2 - Buyer Provided Information
BESS Project
Rev.1 dated 05/16/2025
Ref. No. | Item | Value | Notes
1 | Project Name | By Seller
2 | Project Address [City, County, State] | By Seller
3 | POI Location | By Seller
4 | Project location (latitude/longitude) | By Seller
5 | Expected COD | By Seller
6 | Power @ POI [MW] | By Seller
7 | Duration [hrs] | 4
8 | Interconnection Voltage | By Seller
9 | Interconnection Frequency | 60 Hz
10 | Power Factor | Unity Power Factor +/- 5%
11 | Required Energy type | Lithium-Ion Phosphate
12 | Project Life (years) | 20
13 | Design Life (years) | 20
14 | Maximum Sound Level | 65 dBA | Measured 3 ft from equipment
15 | Design Blackout Duration | 168 hours
16 | Augmentation and Overbuild Strategy | Augmentation Strategy | Bidder must provide in its BESS proposal a reasonably detailed augmentation strategy for the BESS over the project life, including associated pricing. Buyer often sees augmentation intervals of every five years (Years 5, 10, and 15 following COD). Bidder/Seller may propose longer or shorter intervals. Bidder should specify its proposed overbuild approach and the effects of each periodic augmentation on the BESS (including available capacity) if the proposed augmentation strategy is utilized.
17 |  | Overbuild Strategy | Bidder/Seller must offer in its proposal a reasonably detailed overbuild strategy as an alternative to its proposed augmentation strategy for the proposed BESS, with associated pricing. The focus should be on the amount of the proposed capacity overbuild, with the understanding that (i) "overbuild" will be relative to the expected BESS capacity degradation and (ii) the greater the BESS capacity overbuild, the lower the capacity augmentation requirements should be over the project life. Buyer desires for the overbuild strategy to include at least three options with pricing, one for Year 0 overbuild to accommodate a Year 5 augmentation, a second for Year 0 overbuild to accommodate a Year 10 augmentation, and a third for Year 0 overbuild requiring no additional augmentation for the entire 20-year project design life. Please indicate what, if any, affect on the overbuild adjustments would have on the BESS test standards/metrics.
17 | Maximum Inactive Period | 168 hours
18 | Power/Energy Measuring Point | POI / Electrical Interconnection Point
19 | Performance Warranty Period | Per Scope Book
20 | Minimum defective warranty period for all components | Per Scope Book
21 | Required Availability | 100
22 | Required Round Trip Efficiency (RTE) (BESS System-DC) | >90% at Year 0 (beginning of project life) >80% at Y20 (end of project life) | Seller to provide breakdown of Round Trip Efficiency for all components
23 | Required Round Trip Efficiency (RTE) (BESS System-AC) | >85% at BOL and >75% at Y20 | Seller to provide breakdown of Round-Trip Efficiency for all components
24 | BESS Programming language | Open Source and/or password provided with microprocessors and programming outside of China, Russia, Iraq, and North Korea | No BlackBox software
| BESS Available Energy Capacity (AC) Performance Test: | Minimum BESS Available Energy Capacity (AC) = 90% of Target BESS Available Energy Capacity (AC); Guaranteed BESS Available Energy Capacity (AC) = 95% of Target BESS Available Energy Capacity (AC); Target BESS Available Energy Capacity (AC) = [_______] | Applicable
25 | BESS Available Energy Capacity (DC) Performance Test: | Minimum BESS Available Energy Capacity (DC) = 90% of Target BESS Available Energy Capacity (DC); Guaranteed BESS Available Energy Capacity (DC) = 95% of Target BESS Available Energy Capacity (DC); Target BESS Avaialble Energy Capacity (DC) = [_____] | Applicable
26 | BESS Charge Duration Performance Test: | Maximum BESS Charge Duration = 110% of Target BESS Charge Duration; Guaranteed BESS Charge Duration = 105% of Target BESS Charge Duration; Target BESS Charge Duration = [______] | Applicable
27 | BESS Rated Continuous Power Performance Test: | Minimum BESS Rated Continuous Power = 90% of Target BESS Rated Coninuous Power; Guaranteed BESS Rated Coninuous Power = 95% of Target BESS Rated Coninuous Power; Target BESS Rated Coninuous Power = [_______] | Applicable
28 | BESS Auxiiliary Load Performance Test: | Maximum BESS Auxiliary Load = 110% of Target BESS Auxiliary Load; Guaranteed BESS Auxiliary Load = 105% of Target BESS Auxiliary Load; Target BESS Auxiliary Load = [_____] | Not Applicable
29 | BESS Round Trip Efficiency Performance Test: | Minimum BESS Round Trip Efficiency = 90% of Required Round Trip Efficiency (AC); [see item 31] Guaranteed BESS Round Trip Efficiency = 95% of ; Target BESS Round Trip Efficiency = 100% | Applicable
30 | Functional Testing | Per ESIC Section 6.2.1 Self Discharge Rate: Pass/Fail - Self Discharge Rate @ 77 deg F / 25 deg C within +25/-100% of Eq. 6-15 /Eq. 6-17 | Not Applicable
31 |  | Per ESIC Section 6.2.2 Startup and Shutdown Time: Pass/Fail - Startup Time within +/-25% of t_startup and Shutdown Time within +/-25% of t_shutdown (ref Figure 6-10) | Not Applicable
32 |  | Per ESIC Section 6.2.3 Response, Rise, and Settling Time: Response Time within +/-25% of Eq. 6-19, Rise Time within +/- 25% of Eq. 6-23, and Settling Time within +/-25% of Eq. 6-20 | Not Applicable
33 |  | Synchronization - Per ESIC Section 6.2.4 Synchronization: Pass/Fail - must demostrate ability to Synchronize | Applicable
34 |  | Harmonic Distortion - Per ESIC Section 6.2.5 Harmonic Distortion: Pass/Fail - must meet IEEE 519 requirements | Applicable
35 |  | Per ESIC Section 7.1 Charge/Discharge Management: Pass/Fail - per pass criteria in ESIC 7.1.7.1 and 7.1.7.3 | Not Applicable
36 |  | Per ESIC Section 7.2 Peak Load Reduction: Pass/Fail based on successful demonstration | Not Applicable
37 |  | Per ESIC Section 7.3 Microgrid Resiliency for Emergency Conditions: Pass/Fail based on successful demonstration | Not Applicable
38 |  | Per ESIC Section 7.4 Load and Generation Following: Pass/Fail - output must follow setpoint within +/-10% | Not Applicable
39 |  | Per ESIC Section 7.5 Low/High Voltage and Frequency Ride-Through: Pass/Fail - confirm settings per design | Applicable
40 |  | Per ESIC Section 7.6 Volt-VAR Regulation: Pass/Fail - per pass criteria in ESIC 7.6.8 | Applicable
41 |  | Per ESIC Section 8.1.1 Autonomous Frequency Regulation: Pass/Fail - Eq 8-2, Percent Difference is within +/-10% | Not Applicable
42 |  | Per ESIC Section 8.1.2 Autonomous Power Smoothing: Pass/Fail based on successful demonstration | Not Applicable
43 |  | Per ESIC Section 8.1.3 Price-Driven Control Functions: Pass/Fail based on successful demonstration | Not Applicable
44 |  | Per ESIC Section 8.1.4 Temperature Driven Control Functions: Pass/Fail based on successful demonstration | Not Applicable
45 |  | Per ESIC Section 8.2 – Peak Power Limiting: Pass/Fail - output tracks setpoint within +/-10% | Not Applicable
46 |  | Per ESIC Section 8.3 – Black Start: Pass/Fail – demonstrate blackstart capability – inverters function in grid forming mode and maintain load while setting frequency | Not Applicable
47 |  | Per ESIC Section 8.4 – DER Settings to Manage Multiple Grid Configuration: Pass/Fail - demonstrate that parameters are updated | Not Applicable
48 |  | Per ESIC Section 8.5 – Maximum Generation Limit | Not Applicable
49 |  | Per ESIC Section 8.6 – Other Smart Inverter Functions | Not Applicable
50 |  | Per ESIC Section 8.7 – Power Factor: Pass/Fail - output tracks setpoint with +/-10% | Applicable
51 |  | Per ESIC Section 8.8 – Monitoring and Scheduling Control Functions: Pass/Fail - demonstrate paramters change | Not Applicable
52 |  | Per ESIC Section 8.9 – Voltage Support: Pass/Fail based on successful demonstration | Applicable
53 |  | Per ESIC Section 8.10 – Overload Power : Pass/Fail based on successful demonstration | Not Applicable
54 |  | Reserved
55 |  | Reserved
56 |  | Reserved
57 | Primary Application Type | Efficiently maximize MISO capacity accreditation
58 | Primary Operation days/year | 1
59 | Primary Cycles/day | 1
60 | Resting time before discharging (after fully charged) | By Seller to support Primary Application Type
61 | Secondary Application Type
62 | Secondary Operation days/year
63 | Secondary Cycles/day
64 | Resting time before discharging (after fully charged)
65 | Tertiary Application Type
66 | Tertiary Operation days/year
67 | Tertiary Cycles/day
68 | Resting time before discharging (after fully charged)
69 | Quaternary Application Type
70 | Operation days/year
71 | Cycles/day
72 | Resting time before discharging (after fully charged)
73 | [If applicable, other unique project requirements]
74 | [If applicable, other unique project requirements]
75 | [If applicable, other unique project requirements]
76 | [If applicable, other unique project requirements]